## summary and jan09 chart
The very low wind generation period of Jan-09 has ended, after:
* more than 11-1/2 continuous days with total wind gen < 50 MW
< 50 MW: 14-Jan-09 02:43:00 thru 25-Jan-09 17:13:00 (11 days, 14.5 hours)
and
* more than 8-1/2 continuous days < 10 MW.
< 10 MW: 14-Jan-09 16:59:00 thru 23-Jan-09 07:37:00 (8 days, 14.6 hours)
Please see the chart below.
So how often in the past year have we seen others periods of "very low" wind generation ?
The plot on the next tab shows the PerCent of Time By Week Where Total Wind Gen Was < 50 MW (over the last 56 weeks).
The installed wind capacity during this time was ~ 1500 MW, so the 50 MW threshold represents ~ 3% of capacity.
The full 56-week average was ~ 23 %, that is, nearly a quarter of the time the total wind gen was less than 3% of total wind capacity.
Other than the very low wind gen period this month, the weeks of 1/21/08 (55.0 %) and 10/27/08 (53 %) had the next greatest frequency of low wind gen periods.
There was a slight seasonality, with the fall months having somewhat more "very low wind gen" periods.
These very low wind gen periods highlight the high correlation (i.e., low diversity) among wind gen plants within the balancing authority area.
BPA Transmission Technical Operations/TOT/28Jan09

## 1-year lookback chart
Week of 1/19-25/2009: 99.6%
The total installed wind capacity in the BPA balancing authority area during most of this period was approx. 1500 MW, so the 50 MW "very low gen" threshold represents approx 3% of installed capacity; Source: SCADA/PI point 79687
Overall 56-Week Average = 22.8 %

## 1-year lookback data
FREQUENCY OF VERY LOW TOTAL WIND GENERATION
12/31/07 - 1/25/09, By Week (56 Weeks)
BPA TOTAL WIND GENERATION IN THE BALANCING AUTHORITY AREA
THRESHOLD FOR "VERY LOW" WIND GEN = 50 MW
Threshold Represents ~ 3 % of Installed Capacity During This Period
BPA Transmission Technical Operations/TOT/28Jan09
Criterion: | ('AGCDISTB.AGCRPT..MW.79687'<50)
|  | OVERALL 56-Week Average: | 22.78%
Week Begin Date (Mon) | Week End Date | Minutes With Gen < 50 MW | PerCent of Week With Total Wind Gen < 50 MW
2007-12-31 | 2008-01-07 | 2077.2833 | 20.61%
2008-01-07 | 2008-01-14 | 1336.8833 | 13.26%
2008-01-14 | 2008-01-21 | 1877.0167 | 18.62%
2008-01-21 | 2008-01-28 | 5543.45 | 54.99%
2008-01-28 | 2008-02-04 | 40.2 | 0.3988%
2008-02-04 | 2008-02-11 | 0 | 0%
2008-02-11 | 2008-02-18 | 1708.7667 | 16.95%
2008-02-18 | 2008-02-25 | 5098.35 | 50.58%
2008-02-25 | 2008-03-03 | 2916.6 | 28.93%
2008-03-03 | 2008-03-10 | 3218.3167 | 31.93%
2008-03-10 | 2008-03-17 | 1604.1667 | 15.91%
2008-03-17 | 2008-03-24 | 1054.05 | 10.46%
2008-03-24 | 2008-03-31 | 359.9 | 3.57%
2008-03-31 | 2008-04-07 | 3220.2333 | 31.95%
2008-04-07 | 2008-04-14 | 1341.2167 | 13.31%
2008-04-14 | 2008-04-21 | 0 | 0%
2008-04-21 | 2008-04-28 | 1773.15 | 17.59%
2008-04-28 | 2008-05-05 | 2738.35 | 27.17%
2008-05-05 | 2008-05-12 | 1177.8833 | 11.69%
2008-05-12 | 2008-05-19 | 1705.7333 | 16.92%
2008-05-19 | 2008-05-26 | 957.2333 | 9.496%
2008-05-26 | 2008-06-02 | 968.9 | 9.612%
2008-06-02 | 2008-06-09 | 0 | 0%
2008-06-09 | 2008-06-16 | 374.3833 | 3.714%
2008-06-16 | 2008-06-23 | 1757.8667 | 17.44%
2008-06-23 | 2008-06-30 | 974.3 | 9.666%
2008-06-30 | 2008-07-07 | 564.6333 | 5.602%
2008-07-07 | 2008-07-14 | 3213.1 | 31.88%
2008-07-14 | 2008-07-21 | 1387.5333 | 13.77%
2008-07-21 | 2008-07-28 | 525.8833 | 5.217%
2008-07-28 | 2008-08-04 | 1031.3167 | 10.23%
2008-08-04 | 2008-08-11 | 1401.95 | 13.91%
2008-08-11 | 2008-08-18 | 3187.7167 | 31.62%
2008-08-18 | 2008-08-25 | 2122.3833 | 21.06%
2008-08-25 | 2008-09-01 | 0 | 0%
2008-09-01 | 2008-09-08 | 1936.2 | 19.21%
2008-09-08 | 2008-09-15 | 3878.35 | 38.48%
2008-09-15 | 2008-09-22 | 3572.4333 | 35.44%
2008-09-22 | 2008-09-29 | 3651.8833 | 36.23%
2008-09-29 | 2008-10-06 | 3927.7667 | 38.97%
2008-10-06 | 2008-10-13 | 1438.1167 | 14.27%
2008-10-13 | 2008-10-20 | 3484.5333 | 34.57%
2008-10-20 | 2008-10-27 | 1522.8167 | 15.11%
2008-10-27 | 2008-11-03 | 5346.8667 | 53.04%
2008-11-03 | 2008-11-10 | 3576.0333 | 35.48%
2008-11-10 | 2008-11-17 | 3849.8167 | 38.19%
2008-11-17 | 2008-11-24 | 2909.35 | 28.86%
2008-11-24 | 2008-12-01 | 4425.2333 | 43.9%
2008-12-01 | 2008-12-08 | 1830.5333 | 18.16%
2008-12-08 | 2008-12-15 | 905.15 | 8.98%
2008-12-15 | 2008-12-22 | 2663.1 | 26.42%
2008-12-22 | 2008-12-29 | 3275 | 32.49%
2008-12-29 | 2009-01-05 | 1898.35 | 18.83%
2009-01-05 | 2009-01-12 | 0 | 0%
2009-01-12 | 2009-01-19 | 7178.25 | 71.21%
2009-01-19 | 2009-01-26 | 10042.9167 | 99.63%