## Fossil Fuel Summary
FOSSIL FUEL PLANT CAPITAL, O&M, AND COST OF ELECTRICITY SUMMARY (Near Term, 2015)
Technology Category | Black coal |  | Black Coal |  | Black Coal |  | Black coal |  | Black coal |  | Brown coal |  | Brown coal |  | Natural Gas |  | Natural Gas |  | Natural Gas |  | Natural Gas |  | Natural Gas |  | Natural Gas
Description | Integrated Gasification Combined Cycle - without CCS |  | Integrated Gasification Combined Cycle - with CCS |  | Supercritical Pulverised Coal - without CCS |  | Supercritical Pulverised Coal - with CCS |  | Supercritical Pulverised Coal - with oxy-combustion CCS |  | Supercritical Pulverised Coal - without CCS |  | Supercritical Pulverised Coal - with CCS |  | Combined Cycle Gas Turbine - East Coast - without CCS |  | Combined Cycle Gas Turbine - West Coast - without CCSc |  | Combined Cycle Gas Turbine - East Coast - with CCS |  | Combined Cycle Gas Turbine - West Coast with CCSc |  | Open Cycle Gas Turbine - East Coast |  | Open Cycle Gas Turbine - West Coast
Low/High Costa | Low cost | High cost | Low cost | High cost | Low cost | High cost | Low cost | High cost | Low cost | High cost | Low cost | High cost | Low cost | High cost | Low cost | High cost | Low cost | High cost | Low cost | High cost | Low cost | High cost | Low cost | High cost | Low cost | High cost
Total Plant Costb (A$/kW installed) | 3781 | 4621 | 4710 | 5756 | 2408 | 2944 | 4043 | 4941 | 3869 | 4729 | 3214 | 3928 | 5040 | 6160 | 1231 | 1505 | 1354 | 1655 | 2123 | 2595 | 2335 | 2854 | 887 | 1084 | 887 | 1084
Plant Size (MW) | 700-800 | 700-800 | 600-700 | 600-700 | 750 | 750 | 750 | 750 | 750 | 750 | 750 | 750 | 750 | 750 | 600-800 | 600-800 | 300-400 | 300-400 | 600-800 | 600-800 | 300-400 | 300-400 | 160-190 | 160-190 | 160-190 | 160-190
Capacity Factor (%) | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 10% | 10% | 10% | 10%
Auxiliary Load (%) | 17.6% | 17.6% | 23.5% | 23.5% | 9.8% | 9.8% | 23.3% | 23.3% | 31.6% | 31.6% | 10.3% | 10.3% | 23.9% | 23.9% | 2.9% | 2.9% | 2.9% | 2.9% | 15.4% | 15.4% | 15.4% | 15.4% | 1% | 1% | 1% | 1%
Thermal Efficiency (%) | 39% | 39% | 29% | 29% | 38% | 38% | 28% | 28% | 30% | 30% | 35% | 35% | 25% | 25% | 50% | 50% | 50% | 50% | 41% | 41% | 41% | 41% | 33% | 33% | 33% | 33%
Fuel Cost (A$/GJ) | 1.06 | 1.86 | 1.06 | 1.86 | 1.06 | 1.86 | 1.06 | 1.86 | 1.06 | 1.86 | 0.57 | 0.57 | 0.57 | 0.57 | 5.2 | 5.5 | 6.7 | 8.2 | 5.2 | 5.5 | 6.7 | 8.2 | 5.2 | 5.5 | 6.7 | 8.2
Emissions Captured (%) | NA | NA | 89 | 89 | NA | NA | 90 | 90 | 90 | 90 | NA | NA | 90 | 90 | NA | NA | NA | NA | 90 | 90 | 90 | 90 | NA | NA | NA | NA
CO2 Transport and Storage (A$/tCO2) | NA | NA | 19 | 82 | NA | NA | 19 | 82 | 19 | 82 | NA | NA | 7 | 7 | NA | NA | NA | NA | 7 | 21 | 21 | 21 | NA | NA | NA | NA
Fixed O&M (A$/kW-yr) | 73 | 73 | 104 | 104 | 33 | 33 | 55 | 55 | 60 | 60 | 41 | 41 | 67 | 67 | 14 | 14 | 14 | 14 | 25 | 25 | 25 | 25 | 9 | 9 | 9 | 9
Variable O&M (A$/MWh) | 12.8 | 12.8 | 20 | 20 | 4.6 | 4.6 | 15.7 | 15.7 | 9.07 | 9.07 | 5.1 | 5.1 | 16.4 | 16.4 | 2 | 2 | 2 | 2 | 4.2 | 4.2 | 4.2 | 4.2 | 2.5 | 2.5 | 2.5 | 2.5
Plant Life (yrs) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Levelized Cost of Electricity
Fuel Cost | 10 | 17 | 13 | 23 | 10 | 18 | 14 | 24 | 13 | 22 | 6 | 6 | 8 | 8 | 37 | 40 | 48 | 59 | 46 | 48 | 59 | 72 | 57 | 60 | 73 | 89
Variable O&M Cost | 13 | 13 | 20 | 20 | 5 | 5 | 16 | 16 | 9 | 9 | 5 | 5 | 16 | 16 | 2 | 2 | 2 | 2 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3
Fixed O&M Cost | 10 | 10 | 14 | 14 | 4 | 4 | 7 | 7 | 8 | 8 | 6 | 6 | 9 | 9 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 10 | 10 | 10 | 10
CO2 Transport and Storage | 0 | 0 | 19 | 82 | 0 | 0 | 20 | 85 | 18 | 80 | 0 | 0 | 8 | 8 | 0 | 0 | 0 | 0 | 3 | 15 | 10 | 10 | 0 | 0 | 0 | 0
Capital Chargesd | 64 | 78 | 85 | 104 | 37 | 45 | 73 | 89 | 78 | 96 | 50 | 61 | 92 | 112 | 18 | 21 | 19 | 24 | 35 | 43 | 38 | 47 | 105 | 129 | 105 | 129
LCOE (Real 2009-10 A$/MWh) | 96 | 118 | 151 | 242 | 56 | 72 | 130 | 222 | 127 | 215 | 66 | 77 | 134 | 154 | 59 | 65 | 71 | 87 | 91 | 115 | 115 | 136 | 175 | 202 | 191 | 231
a. Factors contributing to low versus high costs include capital, fuel and CO2 disposal costs
b. Based on Table 18 from ACIL Tasman report with a deviation of +/- 10% for high and low cost. Excludes interest during construction.
c. 10% premium assumed for smaller scale CCGT's on the West Coast
d. Based on Weighted Average Cost of Capital of 10.1% (pre-tax real)
Source: Preparation of Energy Market Modelling Data for the Energy White Paper, Supply Assumptions Report. ACIL Tasman, September 2010 http://www.aemo.com.au/planning/0400-0019.pdf
FOSSIL FUEL PLANT CAPITAL, O&M, AND COST OF ELECTRICITY SUMMARY (Long Term, 2030)
Technology Category | Black coal |  | Black Coal |  | Black Coal |  | Black coal |  | Black coal |  | Brown coal |  | Brown coal |  | Natural Gas |  | Natural Gas |  | Natural Gas |  | Natural Gas |  | Natural Gas |  | Natural Gas
Description | Integrated Gasification Combined Cycle - without CCS |  | Integrated Gasification Combined Cycle - with CCS |  | Supercritical Pulverised Coal - without CCS |  | Supercritical Pulverised Coal - with CCS |  | Supercritical Pulverised Coal - with oxy-combustion CCS |  | Supercritical Pulverised Coal - without CCS |  | Supercritical Pulverised Coal - with CCS |  | Combined Cycle Gas Turbine - East Coast - without CCS |  | Combined Cycle Gas Turbine - West Coast - without CCSc |  | Combined Cycle Gas Turbine - East Coast - with CCS |  | Combined Cycle Gas Turbine - West Coast with CCSc |  | Open Cycle Gas Turbine - East Coast |  | Open Cycle Gas Turbine - West Coast
Low/High Costa | Low cost | High cost | Low cost | High cost | Low cost | High cost | Low cost | High cost | Low cost | High cost | Low cost | High cost | Low cost | High cost | Low cost | High cost | Low cost | High cost | Low cost | High cost | Low cost | High cost | Low cost | High cost | Low cost | High cost
Total Plant Costb (A$/kW installed) | 2909 | 3555 | 3353 | 4099 | 2167 | 2649 | 3309 | 4045 | 3080 | 3764 | 2893 | 3535 | 4174 | 5102 | 1053 | 1287 | 1158 | 1416 | 1581 | 1933 | 1739 | 2126 | 785 | 959 | 785 | 959
Plant Size (MW) | 700-800 | 700-800 | 600-700 | 600-700 | 750 | 750 | 750 | 750 | 750 | 750 | 750 | 750 | 750 | 750 | 600-800 | 600-800 | 300-400 | 300-400 | 600-800 | 600-800 | 300-400 | 300-400 | 160-190 | 160-190 | 160-190 | 160-190
Capacity Factor (%) | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 85% | 10% | 10% | 10% | 10%
Auxiliary Load (%) | 17.6% | 17.6% | 23.5% | 23.5% | 9.8% | 9.8% | 23.3% | 23.3% | 31.6% | 31.6% | 10.3% | 10.3% | 23.9% | 23.9% | 2.9% | 2.9% | 2.9% | 2.9% | 15.4% | 15.4% | 15.4% | 15.4% | 1% | 1% | 1% | 1%
Thermal Efficiency (%) | 45% | 45% | 36% | 36% | 48% | 48% | 38% | 38% | 39% | 39% | 47% | 47% | 38% | 38% | 58% | 58% | 58% | 58% | 49% | 49% | 49% | 49% | 40% | 40% | 40% | 40%
Fuel Cost (A$/GJ) | 0.96 | 1.68 | 0.96 | 1.68 | 0.96 | 1.68 | 0.96 | 1.68 | 0.96 | 1.68 | 0.54 | 0.54 | 0.54 | 0.54 | 6.7 | 13.3 | 6.5 | 11.7 | 6.7 | 13.3 | 6.5 | 11.7 | 6.7 | 13.3 | 6.5 | 11.7
Emissions Captured (%) | NA | NA | 89 | 89 | NA | NA | 90 | 90 | 90 | 90 | NA | NA | 90 | 90 | NA | NA | NA | NA | 90 | 90 | 90 | 90 | NA | NA | NA | NA
CO2 Transport and Storage (A$/tCO2) | NA | NA | 19 | 82 | NA | NA | 19 | 82 | 19 | 82 | NA | NA | 7 | 7 | NA | NA | NA | NA | 7 | 21 | 21 | 21 | NA | NA | NA | NA
Fixed O&M (A$/kW-yr) | 73 | 73 | 104 | 104 | 33 | 33 | 55 | 55 | 60 | 60 | 41 | 41 | 67 | 67 | 14 | 14 | 14 | 14 | 25 | 25 | 25 | 25 | 9 | 9 | 9 | 9
Variable O&M (A$/MWh) | 12.8 | 12.8 | 20 | 20 | 4.6 | 4.6 | 15.7 | 15.7 | 9.07 | 9.07 | 5.1 | 5.1 | 16.4 | 16.4 | 2 | 2 | 2 | 2 | 4.2 | 4.2 | 4.2 | 4.2 | 2.5 | 2.5 | 2.5 | 2.5
Plant Life (yrs) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Levelized Cost of Electricity
Fuel Cost | 8 | 13 | 10 | 17 | 7 | 13 | 9 | 16 | 9 | 16 | 4 | 4 | 5 | 5 | 42 | 83 | 40 | 73 | 49 | 98 | 48 | 86 | 60 | 120 | 59 | 105
Variable O&M Cost | 13 | 13 | 20 | 20 | 5 | 5 | 16 | 16 | 9 | 9 | 5 | 5 | 16 | 16 | 2 | 2 | 2 | 2 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3
Fixed O&M Cost | 10 | 10 | 14 | 14 | 4 | 4 | 7 | 7 | 8 | 8 | 6 | 6 | 9 | 9 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 10 | 10 | 10 | 10
CO2 Transport and Storage | 0 | 0 | 15 | 66 | 0 | 0 | 15 | 63 | 14 | 61 | 0 | 0 | 6 | 6 | 0 | 0 | 0 | 0 | 3 | 13 | 8 | 8 | 0 | 0 | 0 | 0
Capital Chargesd | 49 | 60 | 61 | 74 | 33 | 41 | 60 | 73 | 62 | 76 | 45 | 55 | 76 | 93 | 15 | 18 | 17 | 20 | 26 | 32 | 28 | 35 | 93 | 114 | 93 | 114
LCOE (Real 2009-10 A$/MWh) | 79 | 96 | 120 | 191 | 50 | 62 | 107 | 175 | 103 | 170 | 59 | 69 | 112 | 129 | 61 | 105 | 61 | 97 | 86 | 150 | 92 | 137 | 166 | 247 | 165 | 232
a. Factors contributing to low versus high costs include capital, fuel and CO2 disposal costs
b. Based on Table 18 from ACIL Tasman report with a deviation of +/- 10% for high and low cost. Excludes interest during construction.
c. 10% premium assumed for smaller scale CCGT's on the West Coast
d. Based on Weighted Average Cost of Capital of 10.1% (pre-tax real)
Source: Preparation of Energy Market Modelling Data for the Energy White Paper, Supply Assumptions Report. ACIL Tasman, September 2010 http://www.aemo.com.au/planning/0400-0019.pdf